## Slide 1: AWTO Training: Overview of Advanced Water Treatment Technologies and Regulations
November 10, 2022, 10:00 am – 12:00 pm

## Slide 2
CWEA, its Board members and
volunteers are not responsible for the
actions of speakers or the content of their
sessions. No endorsement is implied or
given of any persons or their philosophies,
ideas or statements; nor of any products
or processes; nor of any organizations
or companies who volunteer to serve as
speakers in educational programs.
For reporters: all speakers today are off the record.

## Slide 3: John Rowe, Ph.D
Process Engineer Office of Water Programs at Sacramento State

## Slide 4: Advanced water treatment (AWT)
1-Introduction to AWT Processes

## Slide 5: Objectives
After completion of this webinar, you should be able to:
Define advanced water treatment (AWT), advanced water treatment technology, & reclaimed wastewater
Identify water sources for AWT applications
Identify regulatory rules & framework for AWT
Compare AWT systems
Identify treatment processes that are associated with AWT
Describe critical control points in AWT
Identify critical control points & their purpose

## Slide 6: Definitions
AWT is additional engineered water treatment processes after secondary or tertiary treatment of wastewater to:
1) Remove contaminants of
concern
2) Protect public & environmental
health or meet specific beneficial
reuse parameters
Advanced Treatment Technology (wastewater) is processes capable of reducing specific constituents in wastewater not achieved through other treatment options
Reclaimed water or recycled water is wastewater that is treated to remove solids & impurities for reuse

## Slide 7: Introduction
Water has been used as if supply would not run out
Drought has illuminated conservation of water resources
Water reclamation has increased importance & significance
Strict effluent discharge limits have pushed development of treatment technologies – AWT
https://www.suezwatertechnologies.com/Water/Recycling

## Slide 8: Lake Mead
(castlebaysinks.com)

## Slide 9: Raw Water Sources
All water on earth is potential source of drinking water
Surface water & groundwater are primary sources
Large cities depend on large rivers for water supplies
Reclaimed water use is growing as treatment technologies evolve

## Slide 10: Wastewater Reuse
Reuse of wastewater effluent is not new
Treated wastewater effluent is used in processes where freshwater has been used in past
https://www.suezwatertechnologies.com/Water/Recycling

## Slide 11: Irrigation
Wastewater effluent is used for:
1) Irrigation
2) Industrial make-up water
3) Impoundments for landscaping
4) Gray water systems
5) Wash water
Wastewater effluent can be used for indirect (IPR) & direct (DPR) potable reuse
IPR – AWT effluent discharged to environmental barrier used as water source
DPR – AWT effluent discharged to water distribution
https://www.suezwatertechnologies.com/Water/Recycling

## Slide 12: Wastewater Reuse
Indirect reuse occurs as reclaimed water is discharged to streams, impoundments, or aquifers
In indirect potable reuse, finished effluent is diluted & mixed with freshwater prior to its reuse
news.wef.org
news.wef.org

## Slide 13
Aquifer Recharge Projects
https://www.hillsboroughcounty.org/en/government/county-projects/
https://www.hillsboroughcounty.org/en/government/county-projects/

## Slide 14: Indirect & Unplanned Reuse
Most wastewater reuse is unplanned & indirect reuse (IPR)
Mississippi River receives municipal & industrial wastewater generated between Rocky & Allegheny Mountains
New Orleans produces potable water from mixture of influent
Mississippi River Watershed
news.wef.org
news.wef.org
New Orleans WTP

## Slide 15: Fit-for-Purpose
Diminished water supplies & evolving technology have led to use of reclaimed water
AWT is applied to reused as fit-for-purpose
Fit-for-purpose is reclaimed wastewater that is treated to specific criteria & is reused for purposes according to its treatment
news.wef.org

## Slide 16
Recycle Water Cycle
researchgate.net
DPR
IPR
AWT

## Slide 17: Source Water
In arid regions, increasing uses of wastewater reclamation are occurring
Reuse is part of water resource management strategies
Wastewater reclamation involves treatment to level acceptable for reuse
Ventura County Star

## Slide 18: Indirect Wastewater Reuse
Groundwater aquifers in Los Angeles basin are over-pumped
Treated wastewater is discharged to spreading basins to recharge aquifers
AWT processes allow direct discharge into aquifers & spreading basins of wastewater effluent
Daily Mail

## Slide 19: Water Reuse Treatment
Disinfection
Pre-treatment
Primary
Activated sludge
Clarifier
Chemicals
Sedimentation
Sand filter
MF/UF
Disinfection
Reverse Osmosis
Disinfection/Oxidation (AOP)
Reverse Osmosis
Disinfection/ Oxidation (AOP)
Screening
MBR
Disinfection
Raw Sewage
Conventional Reuse
Indirect Potable Reuse
Indirect Potable Reuse
Advanced Treatment Processes
Advanced Treatment Processes
Reuse
Reuse
Tertiary Treatment
Notes: TREATMENT (Nonpotable)
Proven technology , conservative retrofit: Tertiary filtartion & disinfection of conventional II effluent.
That is the most common treatment, often implemented as retrofit of existing conventional WWTP.
No hi-tech, little R&D needed, extremely reliable, but expensive.
For new reclamation plants, innovative treatment trains exist, more compact and streamlined to operate, such as in particular :
- MBR, for most high quality nonpotable applications
- APT, for agricultural applications

## Slide 20: Reuse Fit-for-Purpose
Reuse water sources include:
1) Municipal wastewater
2) Industry process water
3) Stormwater
4) Agricultural runoff
5) Water from natural resource
extraction
Fit-for-purpose is requirement for water to ensure public health, environmental protection, & specific user needs
Ventura County Star
Ventura County Star

## Slide 21: USEPA
EPA does not require or restrict wastewater reuse
Most states maintain primary regulatory authority over water resources
Most states are establishing programs to address treated wastewater reuse
Ventura County Star

## Slide 22: Awt Processes
Portfolio of treatment options are available for wastewater reuse
Engineered treatment processes remove microbial & chemical contaminants to make possible reuse
Processes:
1) Microfiltration (MF)/
Ultrafiltration (UF)
2) Reverse Osmosis (RO)/
Nanofiltration (NF)
3) Advanced Oxidation (AOP)
4) Biological Aerated Filtration
(BAF)
5) Stabilization
6) Disinfection

## Slide 23: AWT Processes
Advanced Oxidation
Ultraviolet Light
Ozone
Microfiltration/ Ultrafiltration
Reverse Osmosis
Biological Aerated Filtration
Ventura County Star
Ventura County Star
Ventura County Star
Daily Mail
Daily Mail
Daily Mail
Daily Mail

## Slide 24: Wastewater Reuse
Wastewater reuse as potable water is direct or indirect
Indirect reuse involves environmental barrier between reclamation & processing
Direct reuse has direct link between reclamation & processing
Level of treatment depends on end-use of treated water
Daily Mail

## Slide 25
DPR
IPR
Unplanned IPR
IPR– Indirect
Potable Reuse
DPR-Direct
Potable Reuse
Battling Water Scarcity: Direct Potable Reuse Poised as Future of Water Recycling | WaterWorld
30-days

## Slide 26: Potable Reuse Water
Water from AWT trains is discharged into raw water sources upstream of water plant & is retained > 30-days (indirect reuse)
It can be blended with water from treatment plant or introduced into potable distribution system (direct reuse)
Treatment must satisfy drinking water regulations (Safe Drinking Water Act)
Daily Mail
Daily Mail

## Slide 27: Reuse Regulations
California requires 12-10-10-log removal for viruses, & Cryptosporidium & Giardia, respectively
Log removal is reduction or removal of microorganisms
Processes are assigned log reduction levels for microorganisms
Sum of processes are used to comply with 12-10-10-log removals rule
obrag.org

## Slide 28: Log Removal Values (LRV)
Effectiveness of treatment processes are measured using log removal values
Log removals are determined by taking logarithm of ratio of pathogen concentration or contaminate in influent & effluent concentration after treatment process

## Slide 29: Example

## Slide 30: Log Removal value (LRV)
Treatment schemes & process barriers are selected to satisfy water quality requirements influenced by environmental risks, like:
1) Nutrients
2) Aesthetics
3) Risks to human health, like
pathogen removal
Difference between initial wastewater quality & target water quality determines level of treatment required
Treatment target is expressed as LRV
System treatment needs to provide specified LRV

## Slide 31: Reuse Regulations
Conventional wastewater treatment, filtration, & disinfection account for 6-log virus removal credit
Agencies award 1-log of virus removal credit for each month water is retained underground
In California, reuse regulations & site acceptance testing are used to calculate log removals
1) Robustness - expanding variety of
contaminant removal processes in train
2) Reliability - proving degree that processes
are able to remove contaminates
obrag.org

## Slide 32: Advance Water Treatment Processes
MF/UF & RO/NF are more robust filter systems than multimedia filtration
Ozone & UV are reliable disinfection alternatives to chlorine
Ozone is reliable & effective for TOC removal along with RO & Advanced Oxidation (AOP)
AOP removes TOC & is barrier to microorganisms
Multibarrier approach to treatment
AOP
Ozone
obrag.org
obrag.org

## Slide 33: Advanced Water Treatment
Standard treatment train for potable reuse is MF, RO, & UV/H2O2 prior to disinfection, stabilization, & groundwater replenishment
Treatment is defined as full advanced treatment (FAT) by California
Only treatment train currently permitted for groundwater injection in California
Microfiltration
obrag.org

## Slide 34: Advanced Water Treatment Processes
RO trains provide nearly complete total organic carbon (TOC) removal; <0.5 mg/L
RO provides reductions in total dissolved solids (TDS); Conductivity <250 mg/L
MF, RO, & UV/H2O2 provide multiple barriers to pathogens
In UV/H2O2, UV is intended for NDMA mitigation, & H2O2 achieves AOP conditions capable of TOC oxidation
AOP
obrag.org

## Slide 35: Advanced Water Treatment Facilities
Orange County’s Advanced Water Purification Facility is benchmark MF-RO-UV/H2O2 system
San Diego operates system as demonstration (?) facility to validate process for reservoir augmentation
California has only implemented reuse groundwater injection or spreading applications for recharge
obrag.org

## Slide 36
Water Purification Process

## Slide 37: Advanced Water Treatment processes (AWT)
+
= AOP
CONVENTIONAL
WASTEWATER
ENVIRONMENTAL BARRIER
H2O2
UV
AWT Processes

## Slide 38: Critical Control Points (CCP)
Critical control points are unit processes under direct control that require effective policy, procedures, practices, monitoring, & measuring to assure quality requirements
When treating wastewater effluent as reclaimed wastewater hazards will appear
Hazards are presence of contaminates, pathogens, & chemicals

## Slide 39: Critical Control Points
Wastewater reuse systems require multiple barriers to control microbial & chemical contaminants of concern (CEC)
Multiple barriers function through:
1) Robustness - expanding
variety of contaminant
removal processes in train
2) Reliability - proving degree
that processes are able to
remove contaminates

## Slide 40: Critical Control Points (CCP)
Influent quality variability, treatment process upsets, extreme events, & human error affect treatment performance
CCPs are fundamental to design practices & responses for upset events to ensure system reliability
CCP are part of formal framework used to ensure operation quality
Framework is Hazard Analysis & Critical Control Point (HACCP)

## Slide 41: Treatment train for AWT
Storage
Activated Sludge
Effluent
CCP 1
Ammonia
<3 mg/L
Influent
Monochloramine
Acid & Antiscalant
Strainer
CCP 3
Reverse Osmosis
Permeate
Conductivity
<250 mg/L , TOC
<0.5 mg/L
CCP 2
Microfiltration
Pressure Decay
Integrity Test - 5 min
Bubble Test - 0
CCP 4
Advanced Oxidation Peroxide & UV Dose
H2O2
Stabilization
Chlorine
CCP 5
Chlorine Dose (CT)
4-Log Removal - virus
Engineered
Storage
Chlorine
Ammonia 1
Critical Control Points (CCP)
MF
RO
AOP
CT
UV
Effluent

## Slide 42: Additional treatment trains
RO is included in majority of treatment trains for AWT in order to meet TDS goals
Development of non-RO based trains is critical because RO is impractical at inland locations
obrag.org

## Slide 43: Additional treatment trains
Micro-filtration
WW
Reverse
Osmosis
Advanced
Oxidation
Stabilization
Engineered
Storage Storage
WW
WW
WW
WW
WW
WW
Ozone Oxidation
WW
Biological Filtration
WW
Micro-filtration
Reverse Osmosis
WW
WW
Stabilization
WW
WW
Ozone Oxidation
WW
Biological Filtration
WW
Ultra-filtration
WW
Advanced Oxidation
WW
Engineered Storage
WW

## Slide 44: Instrumentation & controls
Instruments & controls are essential for AWT
Instruments:
1) Indicate
2) Measure
3) Monitor
4) Record
5) Control
6) Signal process breakdowns - alarms
Instrumentation & controls are devices that transmit data that allows operators to control treatment functions
obrag.org

## Slide 45: Instrumentation & controls
Central data collection point is main control panel
From control room, operators monitor & control process functions through SCADA system
obrag.org

## Slide 46: Instrumentation & controls
Sophisticated electronics provide automatic controls over process functions
Manual controls backup critical functions
Operators can override automatic systems when necessary
obrag.org

## Slide 47: SCADA system
obrag.org

## Slide 48: Awt Processes
Membrane Filtration (MF, UF, RO)
Ozone
UV Light
Advanced Oxidation
Biological Filtration/Oxidation/Carbon
Activated Carbon

## Slide 49: Membrane filtration processes
Membrane filtration processes are classified on basis of size of particles separated from water stream
Separation technique involves thin, semipermeable membranes that are selective barriers to particles based on molecular size
Membrane blocks passage of large particles & molecules, letting water pass

## Slide 50
Water Molecule
Sugar Molecule
Osmosis
Low Sugar High Sugar
High Water Concentration Low Water Concentration
Water Molecule
Sugar Molecule
Selectively Permeable Membrane
www.bigbrandwater.com

## Slide 51
Reverse Osmosis
Pressure applied > Osmotic Pressure
Semipermeable Membrane
Water Flow
Pure Water
Mineral Concentrated Water
www.bigbrandwater.com

## Slide 52
Osmotic Pressure
> Osmotic Pressure
Water Flow - Osmosis
Water Flow -Reverse Osmosis
Reverse Osmosis - Assignment Point

## Slide 53: Types of membranes
https://www.gotocompletefiltration.com

## Slide 54: Filtration spectrum
Microfiltration
10 um – 100 nm
Ultrafiltration
100 - 10 nm
Nanofiltration
10 - 1 nm
Reverse Osmosis
< 1 nm
Giardia, Crypto,
Bacteria
Giardia, Crypto,
Bacteria
Colloids,
Viruses
Color,
Hardness,
Pesticides, Salts
Colloids,
Viruses,
Color,
Hardness,
Pesticides,
Salts,
Water
Color,
Hardness,
Pesticides,
Salts,
Water
Salts,
Water
Water
Giardia, Crypto,
Bacteria
Colloids,
Viruses
Divalent salts
WERF

## Slide 55: Primary modes of membrane filtration
https://www.gotocompletefiltration.com
Cake Formation
Scouring
https://www.gotocompletefiltration.com

## Slide 56
Waste Stream
High Contaminate Concentration on Membrane
Low Contaminate Level & Water
Membrane Water Treatment
Water Treatment Using Membranes
Semi-permeable Membrane
Contaminates – microbes, organics, minerals, pesticides, CECs, disinfection byproducts
Raw Water
Pure Water
https://www.gotocompletefiltration.com

## Slide 57: Microfiltration (MF)
Microfiltration membrane pores ranging from 0.1 to 2.0 microns
Membrane process is used with settling agents, polymers, & activated carbon to assist in removing constituents
When using membranes, preventing membrane pore blockage by wastestream components is important
MF or UF process is used as pretreatment for RO

## Slide 58: Microfiltration
Removes Pathogens other than virus
WWT Effluent

## Slide 59: Microfiltration
waterworld.com

## Slide 60: Log removal
 | ClNH2 Monochloramine | MF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 11-12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 11-12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 14-15
Log reduction relates to percentage of microorganisms physically removed or inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%

## Slide 61: Ultrafiltration (UF)
UF is most common membrane-based treatment process
Process membrane pore sizes range from 0.005 to 0.1 micron
Particles larger than pores, like emulsified oils, metal hydroxides, proteins, starches, & suspended solids, are retained
Membrane used in membrane bioreactors (MBR)

## Slide 62: MBR
(castlebaysinks.com)
(castlebaysinks.com)
(castlebaysinks.com)

## Slide 63: ultrafiltration
Removes Pathogens & Some Virus
Ultrafiltration
WWT Effluent

## Slide 64: Ultrafiltration
Membrane Bioreactor (MBR)
waterworld.com
waterworld.com

## Slide 65: Log removal
 | ClNH2 Monochloramine | UF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 11-12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 11-12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 14-15
Log reduction relates to percentage of microorganisms physically removed or inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%
Ultrafiltration

## Slide 66: Nanofiltration (NF)
NF uses membrane pore size between UF & RO
Membranes remove divalent salts from water stream
Membrane concentrates components like sugars, nitrogen components, & constituents causing high BOD/COD
Membrane is known as softening membrane
Presently not used in AWT
waterworld.com

## Slide 67: Nanofiltration
waterworld.com

## Slide 68: Reverse osmosis (RO)
Reverse osmosis is tightest membrane process
Membrane allows only water to pass
Membrane retains salts & higher molecular weight components
RO membranes are used for tertiary treatment producing water with low BOD/COD & near-potable water quality
RO is used as post-treatment process following coarser filtration processes like MF or UF
waterworld.com

## Slide 69: Log removal
 | ClNH2 Monochloramine | MF & UF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 11-12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 11-12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 14-15
Log reduction relates to percentage microorganisms physically removed/ inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%

## Slide 70: Reverse osmosis
waterworld.com

## Slide 71: Membrane technology
Microfiltration (MF) & ultrafiltration (UF) are effective in removal of Giardia & Cryptosporidium & bacteria
Reverse osmosis (RO) membranes are used for desalination /demineralization & virus removal
RO membranes are used to remove dissolved organic matter & dissolved contaminants like arsenic, nitrate, pesticides, & radionuclides
waterworld.com

## Slide 72: Ro Membrane
Membrane removes ions like calcium, magnesium, sodium, & chloride
Membrane is used to reduce concentration of natural organic matter (NOM) & to control formation of disinfection byproducts (DBP)
waterworld.com

## Slide 73: Ozone
Ozone is unstable form of oxygen (O3)
Ozone is used to address disinfection, disinfection by-products, taste & odors, color, & micro-coagulation
Ozone reacts to oxidize inorganic compounds like iron, manganese, & sulfides
Difficult-to-oxidize organic compounds include solvents, pesticides, & compounds that cause tastes & odors

## Slide 74: Ozone
Ozone has high disinfectant capacity
Ozone residuals between 0.3 to 2.0 mg/L inactivate viruses
Microorganisms in natural waters are very sensitive to ozone
Giardia & enteric viruses are inactivated by ozone
waterworld.com

## Slide 75: Multiple barrier approach to Treatment
Target | WWTP | MF | RO | UV & Ozone AOP
Protozoa | X | X | X | X
Virus | X |  | X | X
MCLs | X |  | X | X
CECs | X |  | X | X
Target | WWTP | Ozone | BAF | UF | GAC | UV & H2O2 AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X

## Slide 76: Ozone
waterworld.com

## Slide 77: Log removal
 | Ozone | Coagulation/Flocculation | BAF | UV | Cl2 | Total
Virus | 4 | 2 | 1-2 | 4 | 4 | 15-16
Crypto | 2 | 2 | 3-4 | 3 | 0 | 10-11
Giardia | 3 | 2.5 | 2-3 | 3 | 3 | 13.5-14.5
Log reduction relates to percentage microorganisms physically removed/ inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%

## Slide 78: Ultraviolet Light (UV)
Ultraviolet (UV) light is electromagnetic radiation with wavelength shorter than visible light (10 to 400 nm)
Water is disinfected using:
1) UV-C from 200-300 nm
2) UV-B from 280-300 nm
3) Ideal wave length is 254 nm
waterworld.com

## Slide 79: Ultraviolet Light (UV)
UV light damages nucleic acid, preventing microbe replication
Effectiveness of UV light is determined by dose
Dose is calculated as UV intensity multiplied by time of exposure, expressed as millijoule per square centimeter
waterworld.com

## Slide 80: Ultraviolet light
UV light’s effectiveness is based on UV transmittance in water
Transmittance is influenced by UV absorbing organic chemicals
Water must be free of suspended solids, which form deposits on UV lamp sleeves & alter UV transmittance
UV disinfection inactivates viruses
waterworld.com

## Slide 81: Ultraviolet light
waterworld.com

## Slide 82: Log removal
 | Ozone | Coagulation/Flocculation | BAF | UV | Cl2 | Total
Virus | 4 | 2 | 1-2 | 4 | 4 | 15-16
Crypto | 2 | 2 | 3-4 | 3 | 0 | 10-11
Giardia | 3 | 2.5 | 2-3 | 3 | 3 | 13.5-14.5
Log reduction relates to percentage microorganisms physically removed/ inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%
BAF

## Slide 83: Advanced oxidation (AOP)
Advanced oxidation utilizes oxidizing intermediates, like hydroxyl radicals (OH-), to oxidize organic pollutants
Advanced oxidation is used because chemical oxidation takes place slowly in environment
H2O2
Ozone
UV
Ozone
H2O2
UV
AOP
AOP
OH-

## Slide 84: Advanced Oxidation
Facilitates destruction of target pollutants & mineralization of pollutants & byproducts
Treats organic contaminants:
1) Trichloroethylene, perchloroethylene
2) 1,4-dioxane, methyl-tert-butyl ether
  (MTBE), acetone, phenols, N-
  nitrosodimethylamine (NDMA), &
  BTEX
waterworld.com

## Slide 85: Treatment trains - Multiple barrier approach
Target | WWTP | MF | RO | UV & Ozone AOP
Protozoa | X | X | X | X
Virus | X |  | X | X
MCLs | X |  | X | X
CECs | X |  | X | X
Target | WWTP | Ozone | BAF | UF | GAC | UV & H2O2 AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X
4
2
2
3
4
0
6
6
4
0
2
2
6
6
16
11
12
8

## Slide 86: Types of AOP
UV/H2O2 process treats low levels of contaminants:
1) Pesticides
2) Herbicides
3) Endocrine disruption compounds
4) Pharmaceutical products
5) Emerging contaminates (CEC)
Other AOP systems are:
1) O3/H2O2
2) UV/O3
3) HOCl-/UV
waterworld.com

## Slide 87: Types of aop
UV/H2O2 AOPs require UV doses 10-50 times more than for UV disinfection
Water treatment processes that use AOP achieve high levels of pathogen inactivation
UV/ H2O2 systems are used to treat seasonal taste & odor problems as well as organics
waterworld.com

## Slide 88: Log removal
 | ClNH2 Monochloramine | MF & UF | RO | UV/AOP | Cl2 | Total
Virus | 0 | 0 | 1-2 | 6 | 4 | 11-12
Crypto | 0 | 4 | 1-2 | 6 | 0 | 11-12
Giardia | 0 | 4 | 1-2 | 6 | 3 | 14-15
Log reduction relates to percentage microorganisms physically removed/ inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%
AOP

## Slide 89: Advanced oxidation
waterworld.com

## Slide 90: Biological Aerated Filtration
Biological aerated filtration (biofiltration-BAF) is fixed–film process
Biofilm is formed by community of microorganisms (bacteria, fungi, yeast), macro-organisms (protozoa, worms, insect larvae) & extracellular polymeric substances (EPS)
Water is applied intermittently or continuously over media, via up-flow or downflow
Process is aerobic

## Slide 91: Biological aerated filtration
waterworld.com

## Slide 92: Biological aerated filtration
waterworld.com

## Slide 93: Biological filtration/oxidation
Organic matter & water components diffuse into biofilm where treatment occurs through biodegradation
Biofiltration processes are aerobic
Oxygen is supplied to biofilm, concurrently or counter-currently with water flow
Aeration occurs passively by natural flow of air through process or by forced air supplied by blowers
BAC
superiorwater.com

## Slide 94: Biological aerated flooded filter (BAFF)
superiorwater.com

## Slide 95: Biological filtration/Oxidation
Microorganisms' activity is key
Process can maintain performance & rapidly return to initial levels following period of no flow, intense use, toxic shocks, & media backwash
Structure of biofilm protects microorganisms from environmental conditions
It retains biomass inside process
Process control based on empty
bed contact time (EBC - 15min)
Biofilm
superiorwater.com

## Slide 96: Biological filtration/oxidation
Microbial growth attached to filter media (biofilm) consumes organic matter
End products are carbon dioxide, water, biomass, & simple organics
Particle filtration takes place on bare filter media & biofilm
To promote biological activity ozone is added upstream to filter
superiorwater.com

## Slide 97: Biological filtration/oxidation
Ozone may be applied prior to rapid mix, or it may be applied prior to biofilter
Biologically active carbon filters are used in place of conventional filtration, or are downstream of conventional (or membrane) filters
superiorwater.com

## Slide 98: Biological Activated Carbon Filtration (BAC)
Biological activated carbon (BAC) filtration has been used for many years in drinking water treatment, usually after ozonation
Process is able to significantly remove natural organic matter, ozonation transformation products, disinfection by-product precursors, & taste & odor compounds, like geosmin & 2-methylisoborneol

## Slide 99: Biological activated Carbon
Granular activated carbon (GAC) is support material favorable for colonizing of bacteria
Bacteria found in environment are responsible for metabolizing biodegradable organic matter
Combination of ozonation & GAC is referred to as biological activated carbon (BAC) process or biologically enhanced active carbon process

## Slide 100: Biological filtration/Oxidation
Granular Activated Carbon
superiorwater.com
WERF

## Slide 101: Log removal
 | Ozone | Coagulation/Flocculation | BAC | UV | Cl2 | Total
Virus | 4 | 2 | 1-2 | 4 | 4 | 15-16
Crypto | 2 | 2 | 3-4 | 3 | 0 | 10-11
Giardia | 3 | 2.5 | 2-3 | 3 | 3 | 13.5-14.5
Log reduction relates to percentage microorganisms physically removed/ inactivated by given process:
1-log reduction = 90% removal 2-log reduction = 99% 3-log reduction = 99.9% 4-log reduction = 99.99%
superiorwater.com
15 min EBCT

## Slide 102: Activated carbon
Activated carbon is extremely porous & able to readily adsorb, or capture, impurities
Activated carbon attracts known contaminants & naturally dissolved organic matter
Monitoring is needed to ensure that carbon doses are high enough to adsorb contaminants
superiorwater.com

## Slide 103: Multiple barrier approach
Target | WWTP | MF | RO | UV & Ozone AOP
Protozoa | X | X | X | X
Virus | X |  | X | X
MCLs | X |  | X | X
CECs | X |  | X | X
Target | WWTP | Ozone | BAF | UF | GAC | UV & H2O2 AOP
Protozoa | X | X | X | X |  | X
Virus | X | X |  | X |  | X
MCLs | X | X | X |  | X | X
CECs | X | X | X |  | X | X

## Slide 104: Activated carbon
Powdered activated carbon (PAC) is treatment option that is added to treatment system
PAC is useful to treat taste & color deficiencies
PAC is limited to lower removal rates than granular activated carbon (GAC)
superiorwater.com

## Slide 105: Activated carbon
GAC attracts known contaminants & dissolved organic matter
Monitoring is needed to ensure that enough carbon remains active to adsorb contaminants
superiorwater.com

## Slide 106: Adsorption & exchange
Adsorption is physical process where adhesion of atoms, ions, or molecules from gas, liquid, or dissolved solid to carbon surface occurs
Process creates film of adsorbate on surface of adsorbent
superiorwater.com

## Slide 107: Adsorption & Exchange
Adsorbents combine chemical & physical processes to remove organic contaminants & compounds that cause color, taste, & odor
Commonly used adsorbent is activated carbon, granular activated carbon (GAC) & powdered activated carbon (PAC)
superiorwater.com

## Slide 108: Activated carbon
Granular Activated Carbon/Result

## Slide 109: Activated carbon
superiorwater.com

## Slide 110: Ancillary processes in AWT
Corrosion Control Manganese & Iron Removal Critical Control Points

## Slide 111: Corrosion Control & water stabilization
Corrosion is complex involving chemical, electrical, physical, & biological factors
Corrosion is gradual decomposition or destruction of material by chemical action, due to electrochemical reaction
Corrosion caused by:
1) Stray current electrolysis
2) Galvanic corrosion caused by dissimilar metals
3) Differential-concentration cells

## Slide 112: Corrosion cell
Metallic corrosion in potable water is result of electrochemical reaction
Electrochemical reaction is chemical reaction where flow of electric current is essential part of reaction
If electric current is stopped by breaking circuit, chemical reaction will stop
+
-
superiorwater.com

## Slide 113: Corrosion
If chemical reaction is stopped by removing one reacting chemical, flow of electric current will stop
For corrosion to occur, electric current & chemical reaction must be present
superiorwater.com

## Slide 114: Water stabilization
Corrosion from un-stabilized water can be predicted by amount of calcium carbonate saturation
Water is considered to be stable when it is just saturated with calcium carbonate
Two approaches to determine calcium carbonate saturation level
1) Calcium Carbonate Precipitation Potential (CCPP = 0)
2) Langelier Index (+ or -) is indicator of corrosivity of water; it measures
ability of water to dissolve or deposit calcium carbonate; negative
Langelier Index (LI) is corrosive water

## Slide 115: stabilization
To control corrosion, chemicals like polyphosphates can be added to water column
Selection of chemical to achieve calcium carbonate saturation depends on water quality characteristics
superiorwater.com

## Slide 116: Iron & Manganese
Iron & manganese are found in water systems supplied by wells & springs
Iron bacteria can make use of ferrous ion (Fe+2)
Bacteria oxidize iron & use energy for reducing carbon dioxide to organic forms (slimes)
superiorwater.com

## Slide 117: Iron & Manganese
Manganous ion is used similarly by certain bacteria
Small concentrations of iron & manganese can cause problems because bacteria obtain nutrients from water to grow
Iron bacteria are found where combination of dissolved oxygen & dissolved iron are available
Bacterial Slime
superiorwater.com

## Slide 118: Iron & Manganese removal
If water contains manganese up to 0.3 mg/L & less than 0.1 mg/L of iron, effective control is achieved by feeding water with polyphosphates
Chlorine is fed with polyphosphate to prevent growth of iron bacteria
Effect of polyphosphate is to delay precipitation of oxidized manganese
Ion exchange can be used to remove iron & manganese

## Slide 119: Iron & manganese removal
Iron & manganese ion exchange units are downflow pressure filters
Water enters unit through inlet distributor & is forced down through ion exchange resin
Primary advantage of ion exchange for iron & manganese removal is that process requires little attention
Disadvantages are danger of fouling ion exchange resin with oxide

## Slide 120: Ion Exchange for Iron & manganese removal

## Slide 121: Critical control points

## Slide 122: Critical Control Points (CCP)
Critical control points are where failure of standard operations could cause harm to public health; it is points where controls can be applied & hazard prevented, eliminated, or reduced to acceptable
Systematic preventative approach to water safety
Focuses on process barriers rather than end of pipe quality

## Slide 123: Critical Control points (CCP)
Determining critical control points in AWT systems is means used to focus on processes of treatment train that are most important in protecting public health
Points in treatment train where process results are monitored & can be controlled
CCPs are processes in AWT systems that are important for operator training & certification

## Slide 124: Critical control points (CCP)
Activated Sludge
Effluent
CCP 1
Ammonia-3mg/L 1
Monochloramine
Acid & Antiscalant (sequestering agent)
Strainer
CCP 3 Reverse Osmosis
Permeate
Conductivity-250 mg/L,
TOC-0.5 mg/L
CCP 2
Microfiltration
Pressure Decay
Integrity Test-5 minutes, Bubble Test-0 integrity test
CCP 4
Advanced Oxidation Peroxide Dose & UV Dose
H2O2
Stabilization
Chlorine
CCP 5
Chlorine Dose (CT) 4-Log Virus removal (CT)
Engineered
Storage
Chlorine
Ammonia 1
Contact time
WERF
Engineered Storage
30-days

## Slide 125
CCp Limit Triggered

## Slide 126: ccp
When considering reclaimed water as source, engineers are concerned about monitoring because of higher concentrations of pathogens & trace organic chemicals
Multi-barrier approach is advocated so that if problem occurs with one step in process, water is still able to be produced safe

## Slide 127: Multiple barriers
Reuse facilities provide multiple barriers to pathogens & organics (CEC)
Barriers are treatment processes designed to remove particular contaminates of regulatory & public health concern
Specific technologies are employed at AWT facilities that are dependent on local regulations & site-specific requirements
Primary means of meeting low regulatory limits of 0.5 mg/L TOC requires use of RO

## Slide 128
RO
Concentrate
Monitoring Conductivity
Conductivity
superiorwater.com
Influent
Effluent
Treatment Train
Acid Antiscalant
RO
Sequestering
agent

## Slide 129: Monitoring ccp
Process is coupled with monitoring water standards & technology that alerts operators in real-time, if quality falls below standards
Analytical instruments for inline monitoring are improving, allowing operators to stop or divert water, if something is wrong
superiorwater.com

## Slide 130: Multiple barriers
Alternative technologies like ozone & biological aerated filters (BAF) or granular activated carbon (GAC) can be used at locations with higher limits for TOC, like 2-3 mg/L
Non-RO treatment processes are more suitable for inland locations where disposal of RO concentrate is expensive & environmentally challenging

## Slide 131: Multiple barriers
Potable water reuse requires multiple barriers for public safety
Targets in potable reuse treatment strategies are removal of contaminates of emerging concern (CEC), protozoans, viruses, & primary contaminates
Ultrafiltration is designed to remove protozoans & some viruses
Ozone is used to remove protozoans, viruses, primary contaminates, & CEC

## Slide 132: Multiple barriers
Biological aerated filters (BAF) are designed to remove protozoans, primary contaminates, & CEC
Granular activated carbon (GAC) is used to remove primary contaminates & CEC
superiorwater.com

## Slide 133: Multiple barriers
RO, removes protozoans, viruses, primary contaminates, organics, & CEC
Protozoans, viruses, primary contaminates, & CEC are removed in advance oxidation – H2O2/UV
superiorwater.com

## Slide 134
© 2022 California Water Environment Association (CWEA)